MINUTES FOR THE BIDDERS MEETING HELD AT AUDOTORIUM STIMA PLAZA ON THURSDAY, APRIL 10TH , 2014

TENDER NO KPLC1/6D/PT/D/01/14, SUPPLY, INSTALLATION AND COMMISSIONING OF 300KVA ENCLOSED DIESEL GENERATORS AT ELDAS,TAKABA AND RHAMU POWER STATIONS

MEMBERS PRESENT

- Onesmus Maina          - Kenya Power (Chairing)

- Manuel Okoth		- Kenya Power.

- Simon Mbuthia	- Kenya Power  (Taking minutes)

- Haroun Otieno		- Kenya Power.

- Isaac Muriu 		- Belt Cargo Services Ltd

- Timothy Githu 	- Achelis Material Handling Ltd

- Patrick Karanja 	- Southern Corporations Ltd

- Anthony Mwangi	- PowerPoint (EA) Ltd

# The meeting started at 10.30am with introduction centered on Off-Grid Power Stations department operations and areas of activities. The core responsibilities of the department were clearly outlined in order to give the attendants a general overview of its core business areas and expectations.

The following issues were discussed:-

## MIN NO. 1 - GENERAL REQUIREMENTS AND COMPLIANCE WITH THE TENDER DOCUMENT

The tender requirements were clearly outlined as per tender document. The Chairman stressed the need for the bidders to clearly read all instructions on the document and the need to be totally responsive. It was also stated that when submitting their bids, the bidders should ensure that all the required documents such as equipment test reports, design drawings and sketches, catalogues etc must always be attached as they form part of evaluation data.

The bidders were requested to be very keen on other requirements and should be guided by the provided checklist when submitting their bids.

MIN  NO. 2 - TENDER EVALUATION PROCESS

The Chairman stressed the point of submission of tender which is supposed to be in ONE tender system .i.e. Technical and Financial should be bound in one envelop.

The Chairman explained to the bidders how the evaluation process is carried out as most of the bidders present were not conversant with the process. It was stated that the evaluation process is carried out by a team of appointed Kenya Power technical personnel and not by an individual. The process starts with the Technical evaluation which include preliminary evaluation in which items such as bid bond amount, validity etc are certified as well as other requirements outlined are checked. This is followed by the technical evaluation in which the bidder’s conformance with the Kenya power Technical requirements is thoroughly scrutinized. At this stage, the Chairman stressed the need of attaching all the required documents as a proof of their offered equipment’s conformance with required specifications.

On going through the Technical evaluation process, financial evaluation follows. This is then followed by tender award and contract signing.

MIN NO.3 DOWNLOADING OF TENDER DOCUMENT FROM COMPANY WEBSITE

Chairman informed the bidders that downloading tender document from website is free of charge and no fee is charged.

MIN NO.4 THE SITE VISIT

The chairman also clarified that the site visit was not mandatory and was not included on evaluation criteria. However, the bidders were advised to consider visiting Hola station to familiarize themselves with the logistical issues involved as this will guide them in preparation of their bids.

MIN N0.5 PRICES INCLUSIVENESS

The quoted prices by the bidders during tendering must be inclusive of all requirements in the tender document since any omission during price schedule quoting shall be assumed to be covering all the requirements as per the tender document.

MIN N0.6 THE CURRENIES TO BE USED

The chairman clarified that the bidders are free to use their own currencies which is convertible to the Kenya shillings. The conversion rate that shall be used is the prevailing rate at the time of tender closing as per the Central Bank of Kenya.

A.O.B

MIN NO.7  AIR CIRCUIT BREAKER

The bidders ask about the Air Circuit Breaker; and the following clarification was done, that

the correct Rating circuit breaker is 500Amps for the 300KVA instead of the 800Amps as indicated in the tender document.

MIN N0.8 TOOLS- PISTON RING EXPANDER AND PISTON RING COMPRESSOR SLEEVE

The bidders asked whether one can be allowed to deliver some of the tools/Equipment which is combined and the clarification was that, it can be allowed.

MIN N0.9 ON ENGNE SPECIFICATIONS – IN LINE CYLINDER AND WHETHER THE PISTON MUST BE SIX.

The bidder asked whether the engine design must it be In- line cylinder and whether must it be 6 cylinder as there is engine design with 5 cylinders and they still deliver the same power output.

The clarification was that,one is also allowed to deliver engine design with 5 cylinder so long us the prime power output is 300KVA

MIN N0.10 NATIONAL CONSTRUCTION AUTHORITY

Copy of Contractor’s Certificate of Registration for the relevant category from the (and where applicable any other relevant body the User department may deem necessary based on the nature of the work to be carried out by the contractor).

Bidders requested that, they be allowed to submit the receipt for the registration as the indicated that the said Authority has so far not released any certificate to anybody in Kenya.

The clarification is that, during the evaluation the evaluators shall not be very strict as it is a new requirement and therefore case will shall be evaluated individually.

Being no other AOB the meeting ended at 11.00 am.